## Inventory
ETEL Transformer Inventory – Melbourne Stock
Source: MELBOURNE STOCK PDF (nameplate data). Weights and specs are per unit as shown on each nameplate.
Item | Stock description | kVA | Phases | Mounting / type | HV volts (V) | LV volts (V) | Vector group | Cooling | Insulating liquid | Oil (L) | Weight per unit (kg) | Impedance % | Year of manf. | Sample serial no. | SAP ID no. | Supply authority | Qty | Total weight (kg) | Notes
1 | TFR 315KVA 3PH POLEBOLT 22KV/433V NAPHTHENIC OIL | 315 | 3 | Pole-mount | 22000 | 433-250 | Dyn11 | ONAN | Naphthenic | 415 | 1560 | 4.06 | 2025 | 25953-20 | 310083/10042 | Powercor/UE | 19 | 29640
2 | TFR 63KVA 3PH POLEBOLT 22KV/433-250V NAPHTHENIC OIL | 63 | 3 | Pole-mount | 22000 | 433-250 | Dyn11 | ONAN | Naphthenic | 190 | 610 | 3.63 | 2022 | 22659-70 | 310093/10060 | Powercor/UE | 37 | 22570
3 | TFR 100KVA 3PH POLEBOLT 22KV/433-250V NAPHTHENIC OIL | 100 | 3 | Pole-mount | 22000 | 433-250 | Dyn11 | ONAN | Naphthenic | 245 | 900 | 3.8 | 2024 | 24951-11 | 310036/10065 | Powercor/UE | 27 | 24300
4 | TFR 500KVA 3PH POLEBOLT 22KV/433-250V DYN11 EXTERNAL CTS + MDI ESAA INDUSTRIAL | 500 | 3 | Pole-mount, industrial (external CTs + MDI) | 22000 | 433-250 | Dyn11 | ONAN | Not shown | 460 | 1930 | 4.25 | 2014 | 14521-32 |  | Not shown | 2 | 3860 | Plate has no insulating liquid or supply authority listed.
5 | TFR 1500KVA 3PH INDUSTRIAL 6.6KV/433-250V DYN11 ONAN CB | 1500 | 3 | Ground-mount, industrial | 6600 | 433-250 | Dyn11 | ONAN | Mineral oil | 1510 | 5650 | 6.54 | 2023 | 231040-1 |  | Not shown | 1 | 5650 | 6.6 kV primary (not 22 kV). Sound power 55.5 dBA.
6 | TFR 500KVA 3PH GM 22KV/433-250V DYN11 | 500 | 3 | Ground-mount | 22000 | 433-250 | Dyn11 | ONAN | Mineral oil | 860 | 2840 | 3.59 | 2019 | 19653-2 | 310044 | Powercor |  |  | Quantity not stated in stock list.
7 | TFR 500KVA 3PH GM 22KV/433-250V DYN11 HV BUSHING DIN BOLTED | 500 | 3 | Ground-mount, DIN bolted HV bushings | 22000 | 433-250 | Dyn11 | ONAN | Mineral oil | 635 | 2600 | 4.05 | 2017 | 17653-1 | 310044 (S) | Powercor |  |  | Quantity not stated in stock list.
8 | TFR 50KVA 1PH POLEBOLT 22KV 500-250V NAPHTHENIC OIL | 50 | 1 | Pole-mount | 22000 | 500-250 | N/A | ONAN | Mineral oil (per plate) | 115 | 420 | 3.15 | 2024 | 24658-74 | 310050/10059 | Powercor/UE | 16 | 6720 | Stock list says naphthenic oil; plate reads mineral oil. HV/LV material AL/CU.
9 | TFR 25KVA SWER POLEBOLT 12.7KV/500-250V NAPHTHENIC OIL | 25 | 1 | Pole-mount, SWER | 12700 (SWER) | 500-250 | N/A | ONAN | Mineral oil (per plate) | 80 | 280 | 3.33 | 2024 | 24645-22 | 310091/10039 | Powercor/UE | 22 | 6160 | In the PDF this plate appears under item 10. Plate reads mineral oil.
10 | TFR 25KVA 3PH POLEBOLT 22KV/433-250V NAPHTHENIC OIL | 25 | 3 | Pole-mount | 22000 | 433-250 | Dyn11 | ONAN | Naphthenic | 110 | 375 | 3.36 | 2025 | 25950-64 | 310040/10054 | Powercor/UE | 24 | 9000 | Stock list says 1PH, but plate shows 3 phases, Dyn11. In the PDF this plate appears under item 9. HV/LV material CU/AL.
| TOTAL (stated quantities) | [15 empty] | 148 | 107900
| Total kVA capacity (stated quantities) | [16 empty] | 15466
Yellow cells need confirmation (missing quantity or mismatch between stock list and nameplate).